Fire Alarm Plan Review Submittal Requirements

The following is a list of requirements for all plan submittals. Any information that is not provided may result in the plans being rejected and returned without review.

Application

- Completed Application Form with all fields filled-in.

Plans

- Two (2) sets of (paper) plans

Calculations

- Two (2) sets of (paper) calculations

- Two (2) sets of (paper) voltage drop calculations

Specifications

- One (1) set of specification book/books.

- One (1) CD containing all drawings, calculations, and specifications.

50% Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify wiring is strapped up

- Verify notification device back boxes are installed as per the reviewed plans

- Verify initiating device back boxes are installed as per the reviewed plans

Final Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify a record of completion is filled out prior to the test

- Verify communication lines are provided

- Verify a monitoring agreements is signed

- Verify all devices are installed

- Verify a remote annunciator is located within 10’ of the main entrance

- Verify all smoke detectors are at least 2’ from all diffusers

- Verify all smoke detectors are at least 2’ from the tip of all ceiling fan blades

- Verify all duct detectors have the tubes installed properly.  The tube shall have a cap on the end.  The tube shall extend into the opening at least- ¾ of the way.

- Verify a remote test/indicator is provided for all HVAC units above 10’.  Verify the duct detector is properly labeled and corresponds with the readout on the fire alarm panel.

- Test the duct detector with smoke for functionality.  A magnet only test the mechanism

- Verify the breaker is labeled in red

- Verify the electrical panel and breaker is identified in/on the fire alarm panel

- Verify the location of the electrical room is identified in/on the fire alarm panel

- Shut the breaker off to the fire alarm panel, should have an AC Loss

- Disconnect the battery terminal, should battery loss

- Disconnect the communication line, should have communication loss

- Shut the power off to the fire alarm control panel at least 24 hours in advance

- Verify the power is shut off to the fire alarm control panel

- If a sprinkler system is installed, shut the control valve for a supervisory alarm, then test the initiating devices

- Perform a function test for 5 minutes or 15 minutes accordingly

- Verify the fire alarm control room is properly identified.

- Verify a map showing the location of the fire alarm control panel, power supply, hvac units, fire sprinkler riser (if applicable), and Inspector’s Test Valve (if applicable)

- Flow water from the Inspectors Test Valve-Flow identified at panel within 60 seconds.  If the alarm is more than 60 seconds adjust the flow switch setting.  (if applicable)

- A weatherproof horn/strobe is required to be installed in an approved location by the local AHJ (if applicable).  The horn/strobe shall activate upon water flow only. (Not a smoke detector, pull station, duct detector, or hood suppression system)

- Test the low air alarm-identified as trouble at panel. (if applicable)

- Ensure that the pump is properly tested prior to being put in service.  Obtain testing documentation in accordance with NFPA 20 at the time of final inspection.  Ensure that the pump provides the following signals at the fire alarm panel: (if applicable)

  - Pump running

  - Phase Reversal

  - Loss of power

- Verify the alarm was received by the monitoring company and dispatch.

- Verify the appropriate tag is placed on the fire alarm control panel with the correct information

- Verify a green tag is placed on the fire alarm control panel

# Text boxes

STATE OF OKLAHOMA

OFFICE OF THE STATE FIRE MARSHAL