Fire Sprinkler Plan Review Submittal Requirements

The following is a list of requirements for all plan submittals. Any information that is not provided may result in the plans being rejected and returned without review.

Application

- Completed Application Form with all fields filled-in.

Site Plan

- Site Plan showing the location of the entire buildings, water line, fire department connection, and fire hydrant(s).

Plans

- Two (2) sets of (paper) plans

Calculations

- Two (2) sets of (paper) calculations

Specifications

- One (1) set of specification book/books.

- One (1) CD containing all drawings, calculations, and specifications.

50% Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Look at hanger spacing as per NFPA 13 and 13R.

- Look at outlet locations as per the reviewed plans.

- Look at the ceiling/roof elevation changes for proper sprinkler protection.

- Look at ceiling pockets for proper sprinkler protection.

- Look at sky lights for proper sprinkler protection.

- If a fire pump is required and within the building it must be within a 1 hour rated barrier for non-high rise structures.  A 2 hour barrier is required for high rise structures.

Final Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify a record of completion is filled out prior to the test

- Verify the sprinkler system will be monitored by a fire alarm system unless the requirements of IBC 903.4.1 are met.

- Look at outlet locations as per the reviewed plans.

- Look at the ceiling/roof elevation changes for proper sprinkler protection.

- Look at ceiling pockets for proper sprinkler protection.

- Look at sky lights for proper sprinkler protection.

- If a fire pump is required it must be within a 1 hour rated barrier for non-high rise structures.  A 2 hour barrier is required for high rise structures.

- Verify a sprinkler head box with a head wrench or head tool is provided.

- Verify a supply pressure gauge and system pressure gauge is installed.

- Verify a pressure relief valve is installed on all gridded systems. (if applicable)

- Verify a ball drip is installed on the fire department connection.

- Verify the flow switch is installed with the flow arrow going the right direction.

- Verify the Inspector’s Test Valve is installed in a remote location and is properly identified.

- Verify the riser room is properly identified.

- Verify a map showing the location of the fire riser(s)j, Inspector’s Test Valve, and fire alarm panel.

- Verify the Inspector’s Test Valve has an orifice provided in the outside elbow or a test/drain assembly giving the equivalent flow of the smallest sprinkler installed.

- Test the tamper switch(es)-identified as supervisory at panel.

- Flow water from the Inspectors Test Valve-Flow identified at panel within 60 seconds.  If the alarm is more than 60 seconds adjust the flow switch setting.  If after the adjustment a quick opening device or accelerator may be required.

- A weatherproof horn/strobe is required to be installed in an approved location by the local AHJ.  The horn/strobe shall activate upon water flow only. (Not a smoke detector, pull station, duct detector, or hood suppression system)

- Test the low air alarm-identified as trouble at panel. (if applicable)

- Ensure that the pump is properly tested prior to being put in service.  Obtain testing documentation in accordance with NFPA 20 at the time of final inspection.  Ensure that the pump provides the following signals at the fire alarm panel:

  - Pump running

  - Phase Reversal

  - Loss of power

- Shut the tamper switch (if applicable) and continue to test the initiating devices

- Verify the alarm was received by the monitoring company and dispatch.

- Verify the appropriate tag is placed on the riser with the correct information (if applicable)

- Verify a green tag is placed on the fire alarm control panel

# Text boxes

STATE OF OKLAHOMA

OFFICE OF THE STATE FIRE MARSHAL